## Energy Demand
[14 empty] | Building 1 | Building 2 | Building 3 |  |  | Shop |  |  | Lobby
| Time | Fridge | Electric Shower | Air Conditioner | Charging of Devices | Lights | Oven | TV | Dishwasher | Toilet | Total | Total Floor | Total Building | Total | Total | Total | Fridges | Desktop | Total | Air Conditioner | Desktop | Total | Grand Total E |  | Diversified Demand
| (hrs) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) | (kWh) |  |  | Building 1
| 0:00 | 0.030251 | 0 | 0 | 0.316 | 0 | 0 | 0.0005 | 0 | 0 | 0.34675 | 3.4675 | 34.6751 | 34.6751 | 34.6751 | 34.6751 | 1.21 | 0.06 | 1.27 | 0 | 0.3 | 0.3 | 105.5954 |  |  |  | Max Demand | Demand Factor | Total Connected Load
| 1:00 | 0.030251 | 0 | 0 | 0.316 | 0 | 0 | 0.0005 | 0 | 0 | 0.34675 | 3.4675 | 34.6751 | 34.6751 | 34.6751 | 34.6751 | 1.21 | 0.06 | 1.27 | 0 | 0.3 | 0.3 | 105.5954 |  |  |  | (kW) | Residential | (kW)
| 2:00 | 0.030251 | 0 | 0 | 0.316 | 0 | 0 | 0.0005 | 0 | 0 | 0.34675 | 3.4675 | 34.6751 | 34.6751 | 34.6751 | 34.6751 | 1.21 | 0.06 | 1.27 | 0 | 0.3 | 0.3 | 105.5954 |  |  |  | 11.9435 | 0.6 | 19.9058
| 3:00 | 0.030251 | 0 | 0 | 0.316 | 0 | 0 | 0.0005 | 0 | 0 | 0.34675 | 3.4675 | 34.6751 | 34.6751 | 34.6751 | 34.6751 | 1.21 | 0.06 | 1.27 | 0 | 0.3 | 0.3 | 105.5954
| 4:00 | 0.030251 | 0 | 0 | 0.316 | 0 | 0 | 0.0005 | 0 | 0 | 0.34675 | 3.4675 | 34.6751 | 34.6751 | 34.6751 | 34.6751 | 1.21 | 0.06 | 1.27 | 0 | 0.3 | 0.3 | 105.5954 |  |  |  | Max Diversified Demand of Building | Diversity Factor | Sum of max demands
| 5:00 | 0.030251 | 0 | 0 | 0.316 | 0 | 0 | 0.0005 | 0 | 0 | 0.34675 | 3.4675 | 34.6751 | 34.6751 | 34.6751 | 34.6751 | 1.21 | 0.06 | 1.27 | 0 | 0.3 | 0.3 | 105.5954 |  |  |  | (kW) | 50 to above apartments | (kW)
| 6:00 | 0.030251 | 0 | 0 | 0.316 | 0 | 0 | 0.0005 | 0 | 0 | 0.34675 | 3.4675 | 34.6751 | 34.6751 | 34.6751 | 34.6751 | 1.21 | 0.06 | 1.27 | 0 | 0.3 | 0.3 | 105.5954 |  |  |  | 477.738 | 0.4 | 1194.3451
| 7:00 | 0.030251 | 0 | 6 | 0.316 | 0 | 0 | 0.0005 | 0 | 0 | 6.3468 | 63.4675 | 634.6751 | 634.6751 | 634.6751 | 634.6751 | 1.21 | 0.06 | 1.27 | 18 | 0.3 | 18.3 | 1923.5954
| 8:00 | 0.030251 | 4.75 | 6 | 0.316 | 1 | 0 | 0.0005 | 0 | 0 | 12.0968 | 120.9675 | 1209.6751 | 1209.6751 | 1209.6751 | 1209.6751 | 1.21 | 0.06 | 1.27 | 18 | 1 | 19 | 3649.2954
| 9:00 | 0.030251 | 0 | 6 | 0 | 1 | 0 | 0.0005 | 0 | 0 | 7.0308 | 70.3075 | 703.0751 | 703.0751 | 703.0751 | 703.0751 | 1.21 | 0.2 | 1.41 | 18 | 1 | 19 | 2129.6354 |  |  | Building 2
| 10:00 | 0.030251 | 0 | 6 | 0 | 1 | 0 | 0.0005 | 0 | 0 | 7.0308 | 70.3075 | 703.0751 | 703.0751 | 703.0751 | 703.0751 | 1.21 | 0.2 | 1.41 | 18 | 1 | 19 | 2129.6354 |  |  |  | Max Diversified Demand of Building
| 11:00 | 0.030251 | 0 | 6 | 0 | 1 | 0 | 0.0005 | 0 | 0 | 7.0308 | 70.3075 | 703.0751 | 703.0751 | 703.0751 | 703.0751 | 1.21 | 0.2 | 1.41 | 18 | 1 | 19 | 2129.6354 |  |  |  | (kW)
| 12:00 | 0.030251 | 0 | 6 | 0 | 1 | 0 | 0.0005 | 0 | 0 | 7.0308 | 70.3075 | 703.0751 | 703.0751 | 703.0751 | 703.0751 | 1.21 | 0.2 | 1.41 | 18 | 1 | 19 | 2129.6354 |  |  |  | 477.738
| 13:00 | 0.030251 | 0 | 6 | 0 | 1 | 0 | 0.0005 | 0 | 0 | 7.0308 | 70.3075 | 703.0751 | 703.0751 | 703.0751 | 703.0751 | 1.21 | 0.2 | 1.41 | 18 | 1 | 19 | 2129.6354
| 14:00 | 0.030251 | 0 | 6 | 0 | 1 | 0 | 0.0005 | 0 | 0 | 7.0308 | 70.3075 | 703.0751 | 703.0751 | 703.0751 | 703.0751 | 1.21 | 0.2 | 1.41 | 18 | 1 | 19 | 2129.6354 |  |  | Building 3
| 15:00 | 0.030251 | 0 | 6 | 0 | 1 | 0 | 0.0005 | 0 | 0 | 7.0308 | 70.3075 | 703.0751 | 703.0751 | 703.0751 | 703.0751 | 1.21 | 0.2 | 1.41 | 18 | 1 | 19 | 2129.6354 |  |  |  | Max Diversified Demand of Building
| 16:00 | 0.030251 | 0 | 6 | 0 | 1 | 0 | 0.0005 | 0 | 0 | 7.0308 | 70.3075 | 703.0751 | 703.0751 | 703.0751 | 703.0751 | 1.21 | 0.2 | 1.41 | 18 | 1 | 19 | 2129.6354 |  |  |  | (kW)
| 17:00 | 0.030251 | 4.75 | 6 | 0 | 1 | 0 | 0.0005 | 0 | 0 | 11.7808 | 117.8075 | 1178.0751 | 1178.0751 | 1178.0751 | 1178.0751 | 1.21 | 0.2 | 1.41 | 18 | 1 | 19 | 3554.6354 |  |  |  | 477.738
| 18:00 | 0.030251 | 0 | 0 | 0 | 1 | 0 | 0.0195 | 0 | 0 | 1.0498 | 10.4975 | 104.9751 | 104.9751 | 104.9751 | 104.9751 | 1.21 | 0.2 | 1.41 | 0 | 1 | 1 | 317.3354
| 19:00 | 0.030251 | 0 | 0 | 0 | 1 | 2 | 0.0195 | 0 | 0 | 3.0498 | 30.4975 | 304.9751 | 304.9751 | 304.9751 | 304.9751 | 1.21 | 0.06 | 1.27 | 0 | 0.3 | 0.3 | 916.4954 |  |  | Lobby+Shop
| 20:00 | 0.030251 | 0 | 0 | 0 | 1 | 2 | 0.0195 | 0 | 0 | 3.0498 | 30.4975 | 304.9751 | 304.9751 | 304.9751 | 304.9751 | 1.21 | 0.06 | 1.27 | 0 | 0.3 | 0.3 | 916.4954 |  |  |  | Max Demand | Demand Factor | Total Connected Load
| 21:00 | 0.030251 | 0 | 0 | 0.316 | 0 | 0 | 0.0195 | 1.04 | 0 | 1.4058 | 14.0575 | 140.5751 | 140.5751 | 140.5751 | 140.5751 | 1.21 | 0.06 | 1.27 | 0 | 0.3 | 0.3 | 423.2954 |  |  |  | (kW) | airport/bank/shop | (kW)
| 22:00 | 0.030251 | 0 | 0 | 0.316 | 0 | 0 | 0.0195 | 0 | 0 | 0.36575 | 3.6575 | 36.5751 | 36.5751 | 36.5751 | 36.5751 | 1.21 | 0.06 | 1.27 | 0 | 0.3 | 0.3 | 111.2954 |  |  |  | 12.246 | 0.6 | 20.41
| 23:00 | 0.030251 | 0 | 0 | 0.316 | 0 | 0 | 0.0005 | 0 | 0 | 0.34675 | 3.4675 | 34.6751 | 34.6751 | 34.6751 | 34.6751 | 1.21 | 0.06 | 1.27 | 0 | 0.3 | 0.3 | 105.5954
Pumphouse
Load |  | 0.030251 | 9.5 | 6 | 0.316 | 1 | 2 | 0.0195 | 1.04 | 0 | [6 empty] | 1.21 | 0.2 |  | 18 | 1 |  | E daily (kWh) | E daily (MWh) |  |  | Max Demand
[23 empty] | 29694.2893 | 29.6943 |  |  | (kW)
82
| Alterations | [24 empty] | OVERALL
|  | Cut night time air conditioning | [24 empty] | 1527.4601 | kW
|  | Alter flats so only cooled for 21000BTU / 6.3kW required alone |  |  |  |  | https://www.appliancesonline.com.au/product/kelvinator-6kw-window-box-reverse-cycle-air-conditioner-kwh62hre | [8 empty] | 6kw appliance chosen
|  | Alter Lobby, 20 people max, hot, well insulated, produces result of 19000W required. | [6 empty] | https://www.calculator.net/btu-calculator.html?roomsize1=300&roomwidthunit=meters&ceilingheight1=3&ceilingheight1unit=meters&people1=20&roomtype1=house&insulation1=good&sunexposure1=normal&climate1=hot&ctype=room&x=64&y=33
[9 empty] | https://www.appliancesonline.com.au/product/kelvinator-6kw-window-box-reverse-cycle-air-conditioner-kwh62hre | [12 empty] | 3* 6kw devices chosen

## Solar Field
Solar Field Specs |  |  |  | Hydrogen Only System Size |  |  |  | Electrolyser Requirement Daily
| Area per kW of panel | 6.64 | m^2 kW^-1 |  | Area per kW of panel | 6.64 | m^2 kW^-1 | 134.5151 | MWh
| Total System Capacity | 10000 | kW |  | Total System Capacity | 30000 | kW
| Pricing of panels | 600 | £ per kW of panelling |  | Pricing of panels | 600 | £ per kW of panelling
| Area of system | 66400 | m^2 |  | Area of system | 199200 | m^2
|  | 0.0664 | km^2 |  |  | 0.1992 | km^2
| Price of system | 6000000 | £ |  | Price of system | 18000000 | £
|  | 6 | mill£ |  |  | 18 | mill£
| Average daily production | 45.5145 | MWh |  | Average daily production | 136.5435 | MWh

## Electrolysers
Electrolyser Specs |  | https://nelhydrogen.com/product/m-series/ |  |  |  | E required daily overall | 29694.2893 | kWh
| E required: | 4.53 | kWh/Nm³ |  |  | Hydrogen Required Daily Overall | 2512.1369 | kg
| Max output: | 207 | Nm³/h |  |  |  | 28750.0109 | Nm^3
|  | 14.375 | kg /h
| Dimensions | 160 | m^2
| Theoretical H2O consumption | 4.5 | kg kg^-1
| Theoretical H2O consumption | 4.5 | L kg^-1
| Theoretical H2O consumption | 0.0045 | m^3 kg^-1
Electrolysers Required | [6 empty] | 1 machine can handle
| Water | [5 empty] | 937.71 | kWh an hour
|  | H2O used daily | 11304.6159 | kg |  |  | producing
|  |  | 11304.6159 | L |  |  | 207 | Nm3 hr-1
|  |  | 11.3046 | m^3
[7 empty] | 937.71 | kWh over 1 hour
Electricity
|  | E from Solar daily | 134515.1306 | kWh
|  |  | 134.5151 | MWh
Number of Electrolysers
|  | Hours in sunlight | 6 | hrs
|  | 1 Machine for 6hrs | 1242
|  | Nr of machines required | 23.1482
Basically 23
M400 produces double the amount per hour as the regular m200, thus can halve the number required but not the price as this is dependent upon kW.
|  | 992 cm x 82 cm x 214 cm | M400 DIMENSIONS |  | 332 cm x 58 cm x 208 mm
|  | 9.9 | m | long | 3
|  | 0.8 | m | high | 0.5
|  | 2 | m | wide | 2
|  | 19.8 | m^2

## H2 Stores
Storage Unit Specs
| Website | https://nelhydrogen.com/product/hydrogen-supply-storage-ss001/ |  | kg hydrogen used daily | 2512.1369 | kg
| Dimensions | L: 12300mm W: 2400mm H: flexible 600-3000mm
| Max storage possible | 500 | kg
System required
5.0243
5 storage vessels required at minimum for a days operation

## Fuel Cells
Fuel Cell Specs |  |  |  |  | E Required Daily Overall | 29694.2893 | kWh
| Output | 200 | kW
| Consumption | 4.7 | g s^-1 |  | Overall Diversified Demand | 1527.4601 | kW
| Consumption | 0.0047 | kg s^-1
| Consumption | 0.053789 | Nm^3 s^-1
One machine
producing
a days
consumption
would use: | Equivalent hours work | 148.4714 | hrs
| Equivalent seconds | 534497.2077 | s
| Nm^3 Used | 28750.0109 | Nm^3
| kg Used | 2512.1369 | kg
Number of
fuel cells | [6 empty] | Rough Working
required for
diversified peak | [6 empty] | 200 | kW
demand: | Number required: | 7.6373 | fuel cells |  |  |  | 1 | hr
| Number practically: | 8 | fuel cells |  |  |  | 3600 | secs
| Practical max product: | 1600 | kW
[7 empty] | 193.64 | Nm^3
[7 empty] | 200 | kWh
| https://www.ballard.com/docs/default-source/motive-modules-documents/hd_motive_brochure_pgs_072517-01.pdf?sfvrsn=2 | [5 empty] | 0.9682 | Nm^3
| 1200 x 869 x 506 mm | for a 100kW cell |  | 1.2 | m |  | 1 | kWh
| Assume it is double for the 200kW fuel cell. |  |  | 0.869 | m
|  |  |  | 0.506 | m
|  |  |  | 1.0428 | m^2
|  |  |  | 0.52766 | m^3
Thus for 200kW::
|  |  |  | 1.0553 | m^3
|  |  |  | 2.0856 | m^2
Area taken up by fuel cells: |  | 16.6848 | m^2